## Wind Pump BoQ - summary
Kiritimati Wind Pump Installation & Rehabilitation BoQ - summary
# | Item | Unit | Quantity
1. Southern Cross sub-assemblies
1.01 | 30ft high 3-post hot-dip galvanised tower to suit a 10ft Southern Cross Windmill, with anchors, ladder and safety platform | set | 1
1.02 | 10ft Southern Cross windmill 3-post (gearbox, wheel, tail and stub tower) with hot-dipped GI fan blades and brackets | set | 1
1.03 | 30ft tower connecting drive rods with cross guides and forks | set | 2
2. Yellowtail sub-assemblies
2.01 | Yellowtail complete 10ft windwheel with hot-dipped GI fan blades and brackets | set | 4
2.02 | Yellowtail 40ft tower connecting drive rods with cross guides and forks | set | 6
3. Gearbox Parts
3.01 | White metal bearings for Yellowtail 10ft gearbox (set of 4) | set | 2
3.02 | Crosshead spindle for Yellowtail 10ft gearbox | ea | 2
3.03 | Shell Omala 150 Oil - 20L drum | drum | 4
4. Tower parts
4.01 | 3 anchor posts, 6 anchor plates HDGI (50/50/5 angle iron) with SS bolts, compatible with 30ft Aermotor tower | set | 1
4.02 | Furling pull-out wire rope with grips, SS, 3 - 4mm x 13m | length | 9
4.03 | Pull-out/furl handle for Yellowtail tower | ea | 2
4.04 | Cold galvanised paint, brushable, for tower and windwheel, 4L | tin | 9
4.05 | SS bolt with nut for Yellowtail tower (M10) | ea | 90
5. Pumping sub-assemblies
5.01 | 3” x 12” stroke cast iron syphon pump, with brass pump and 1-3/8" x 12" compensator, with SS baseplate bolts | set | 5
5.02 | Intake: 2" foot valve F, 2 x 2" x 50mm PE M adaptor, 2" PE elbow, 2" PE pipe for up to 4m deep setting | set | 8
5.03 | Outlet: 2" plastic air chamber with 2 x 2" horizontal check valves, 2" tee with 3/4" offtake, 2" nipples | set | 6
6. Pump parts
6.01 | 1-3/8” x 12” stroke brass compensator complete | set | 2
6.02 | 1-3/8" leather compensator buckets | pair | 45
6.03 | 3" leather pump buckets | pair | 30
6.04 | White compensator rod centralizing bush | ea | 10

## Wind Pump BoQ - detailed
| Kiritimati Island Wind Pump Installation & Rehabilitation BoQ - detailed |  | Quantity
| Item | Unit | DG1W | DG2W | DG2E | DG3C | DG3E | FWG3W | BG1W | BG1E | BG2E | BG3W | NZG1E | Spare | Sub-total quantity | Current useable inventory | Total quantity to be procured | Notes
| Model |  | Y/Tail | Y/Tail | Y/Tail | Y/Tail | Y/Tail | Y/Tail | Y/Tail | Y/Tail | S/Cross | A/Motor | Y/Tail
| Rehabilitate, decommission or new build |  | Decom | Rehab | Rehab | Decom | Decom | Rehab | Rehab | Rehab | New | Rehab | Rehab
1. Southern Cross Sub-Assemblies
1.01 | 30ft high 3-post tower to suit a 10ft Southern Cross Windmill, with anchors, ladder and safety platform | set | [8 empty] | 1 |  |  |  | 1 |  | 1
1.02 | 10ft Southern Cross windmill 3-post (gearbox, wheel, tail and stub tower) with hot-dipped GI fan blades & brackets | set | [8 empty] | 1 |  |  |  | 1 |  | 1
1.03 | 30ft tower connecting drive rods with cross guides and forks | set | [8 empty] | 1 | 1 |  |  | 2 |  | 2
2. Yellowtail Sub-Assemblies
2.01 | Yellowtail complete 10ft windwheel with hot-dipped GI fan blades and brackets | set | [6 empty] | 1 | 1 |  |  |  | 2 | 4 |  | 4
2.02 | Yellowtail 40ft tower connecting drive rods with cross guides and forks | set |  | 1 | 1 |  |  | 1 | 1 | 1 |  |  | 1 |  | 6 |  | 6
3 Gearbox Parts
3.01 | White metal bearings for Yellowtail 10ft gearbox (set of 4) | set | [11 empty] | 2 | 2 |  | 2
3.02 | Crosshead spindle (part #27) | ea | [11 empty] | 2 | 2 |  | 2 | If clunky gearbox
3.03 | Shell Omala 150 Oil - 20L drum | drum |  | 0.2 | 0.2 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 2 | 4 |  | 4 | 4L per gearbox
4 Tower Parts
4.01 | 3 anchor posts, 6 anchor plates HDGI (50/50/5 angle iron) with SS bolts | set | [9 empty] | 1 |  |  | 1 |  | 1
4.02 | Furling pull-out wire rope with grips, SS, 3 - 4mm x 13m | length |  | 1 | 1 |  |  | 1 | 1 | 1 |  | 1 | 1 | 2 | 9 |  | 9 | Not "soft bundling wire"
4.03 | Pull-out/furl handle (part #48) | ea | [7 empty] | 1 |  |  |  | 1 | 2 |  | 2 | Bolts to side of tower near base
4.04 | Cold galvanised paint, brushable, for tower and windwheel, 4L | tin |  | 1 | 1 |  |  | 1 | 1 | 1 |  | 1 | 1 | 2 | 9 |  | 9
4.05 | SS bolt with nut for tower (M10) | ea |  | 10 | 10 |  |  | 10 | 10 | 10 |  |  | 10 | 30 | 90 |  | 90
5. Pumping sub-assemblies
5.01 | 3” x 12” stroke cast iron syphon pump, with brass pump and 1-3/8" x 12" compensator, with SS baseplate bolts | set | [6 empty] | 1 | 1 | 1 | 1 |  | 1 | 5 |  | 5
5.02 | Intake: 2" foot valve F, 2 x 2" x 50mm PE M adaptor, 2" PE elbow, 2" PE pipe for up to 4m deep setting | set | [6 empty] | 1 | 1 | 1 | 1 |  | 4 | 8 |  | 8
5.03 | Outlet: 2" plastic air chamber with 2 x 2" horizontal check valves, 2" tee with 3/4" offtake, 2" nipples | set | [6 empty] | 1 | 1 | 1 | 1 |  | 2 | 6 |  | 6
6. Pump Parts
6.01 | 1-3/8” x 12” stroke brass compensator complete | set |  | 1 | [9 empty] | 1 | 2 |  | 2 | Same as current pumps
6.02 | 1-3/8" leather compensator buckets | pair |  | 1.5 | 1.5 |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 35 | 47 | 2 | 45 | 3 per compensator
6.03 | 3" leather pump buckets | pair |  | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 38 | 8 | 30 | 2 per pump
6.04 | White compensator rod centralizing bush | ea | [11 empty] | 10 | 10 |  | 10 | Fits into top of compensator
| Issues |  | Squeaking (need oil). | Compensator leaking lots. | Oil leaking from bottom of gearbox. | No compensator. | Dismantle and use for spares. | Oil leaking down pump rod. | Oil leaking down pump rod. | Compensator leaking lots. |  | Tower to be recentred
|  |  | Source local timber for maintenance platform. |  | Need to tighten some loose nuts. | No pump rod. | No windwheel. | Ladder bolts missing. | Compensator leaking lots. | No flow to main line.
|  |  | Timber guides to be realigned/replaced. |  | Gearbox wobbling around. |  | No compensator. |  | 3/4" offtake thread gone. | Water available from offtake.
|  |  | Oil leaking from bottom of gearbox. |  |  |  | Gearbox looks OK - keep for spare. |  | Air chamber old & rusted.
[7 empty] | Oil splattered on nearby solar panels. |  | Barely any water being pumped (if any)